## Instructions
SunSpec PICS Template
This SunSpec PICS template was generated by SunSpec Dashboard v0.0.0 based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. Some points require a value range be specified. Points that have a grey background in the Min and Max column must
have a minimum and maximum value specified in the Min and Max columns. The value should be the value with the scale
factor applied. For example, a value specified in these fields would be 97.34 not 9734 if the scale factor is -2.
For models that have repeating elements, the value range is specified on the points in the first element and are
applicable for all of the repeating elements.
4. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## OEM Lux Product Info
Product Information
Product Type | Inverter
Manufacturer Name | ShenZhen Lux Power Technology Co., LTD
Product Name | Hybrid inverter
Product Model Numbers | LXP-LB-US xK GEN-LB-US xK x: may be 5/7.6/8/9.6/10/11.4/12/13/15/16, x is a number less than 16.
Submitter Information
Full Name | Guangyan
Job Title | Manager
Company Name | ShenZhen Lux Power Technology Co., LTD
Relationship to Manufacturer | Employee
Email
Phone
Device Under Test Information
Test Type | SunSpec Modbus Conformance Certification
Firmware Version Tested | fA1.0 (or FA1.0)
Firmware Checksum (in hex) | HybridDSP_Date.Hex checksum: 0x55414132 HybridM0_Date.Hex checksum: 0x55424233 HybridApp_Data.Hex checksum: 0x55434334
Interface Type | Modbus TCP
If RTU
Interface Name
Unit ID
Baud Rate
Parity | None
Timeout (secs)
If Modbus TCP
IP Address | 119.145.35.9
IP Port | 502
Unit ID | 1
If IEEE 2030.5
IP Address
IP Port
Poll Rate
Client PIN
Timeout (secs)
Reserved For SunSpec Alliance
SunSpec Certificate Number | SM-000042
Certificate Signer Name | Dylan Tansy
Certificate Issued Date | 2025-04-28
Certificate Archive Location | https://sunspec.org/wp-content/uploads/2009/03/Shenzhen-Lux-Power_Modbus-for-IEEE-1547_Certificate_SM000042.pdf

## White Label EG4 Product Info
Product Information
Product Type | Inverter
Manufacturer Name | EG4 Electronics LLC
Product Name | Hybrid Inverter
Product Model Numbers | 18kPV-12LV or IV-12000-HYB-AW-XX, XX is a number between 00-99 IV-8000-HYB-AW-XX, XX is a number between 00-99 IV-16000-HYB-AW-FX-XX, XX is a number between 00-99 IV-13000-HYB-AW-FX-XX, XX is a number between 00-99
Submitter Information
Full Name | Eliud Gonzalez
Job Title | Jr. Firmware Engineer
Company Name | EG4 Electronics
Relationship to Manufacturer | Employee
Email
Phone
Device Under Test Information
Test Type | SunSpec Modbus Conformance Certification
Firmware Version Tested | fA1.0 (or FA1.0)
Firmware Checksum (in hex) | HybridDSP_Date.Hex checksum: 0x55414132 HybridM0_Date.Hex checksum: 0x55424233 HybridApp_Data.Hex checksum: 0x55434334
Interface Type | Modbus TCP
If RTU
Interface Name
Unit ID
Baud Rate
Parity | None
Timeout (secs)
If Modbus TCP
IP Address | 119.145.35.9
IP Port | 502
Unit ID | 1
If IEEE 2030.5
IP Address
IP Port
Poll Rate
Client PIN
Timeout (secs)
Reserved For SunSpec Alliance
SunSpec Certificate Number | SM-000042
Certificate Signer Name | Tom Tansy
Certificate Issued Date | 2025-06-02
Certificate Archive Location | https://sunspec.org/wp-content/uploads/2009/03/EG4-White-Label_Shenzhen-Lux-Power_Modbus-for-IEEE-1547_Certificate_SM000042.pdf

## 1
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50002 | ID |  | 1 | R
50003 | L |  | 66 | R
50004 | Mn |  | Luxpower | R
50020 | Md |  | 00095A00 | R
50036 | Opt |  | opt_a_b_c | R
50044 | Vr |  | V001 | R
50052 | SN |  | Walter0002 | R
50068 | DA |  | supported | RW | 0 | 150
50069 | Pad |  | 0 | R

## 701
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50070 | ID |  | 701 | R
50071 | L |  | 153 | R
50072 | ACType |  | supported | R
|  | SINGLE_PHASE | supported
|  | SPLIT_PHASE | supported
|  | THREE_PHASE | supported
50073 | St |  | supported | R
|  | OFF | supported
|  | ON | supported
50074 | InvSt |  | supported | R
|  | OFF | supported
|  | SLEEPING | supported
|  | STARTING | supported
|  | RUNNING | supported
|  | THROTTLED | supported
|  | SHUTTING_DOWN | supported
|  | FAULT | supported
|  | STANDBY | supported
50075 | ConnSt |  | supported | R
|  | DISCONNECTED | supported
|  | CONNECTED | supported
50076 | Alrm |  | supported | R
|  | GROUND_FAULT | supported
|  | DC_OVER_VOLT | supported
|  | AC_DISCONNECT | supported
|  | DC_DISCONNECT | supported
|  | GRID_DISCONNECT | supported
|  | CABINET_OPEN | supported
|  | MANUAL_SHUTDOWN | supported
|  | OVER_TEMP | supported
|  | OVER_FREQUENCY | supported
|  | UNDER_FREQUENCY | supported
|  | AC_OVER_VOLT | supported
|  | AC_UNDER_VOLT | supported
|  | BLOWN_STRING_FUSE | supported
|  | UNDER_TEMP | supported
|  | MEMORY_LOSS | supported
|  | HW_TEST_FAILURE | supported
|  | MANUFACTURER_ALRM | supported
50078 | DERMode |  | unimplemented | R
|  | GRID_FOLLOWING | unimplemented
|  | GRID_FORMING | unimplemented
|  | PV_CLIPPED | unimplemented
50080 | W |  | supported | R
50081 | VA |  | supported | R
50082 | Var |  | supported | R
50083 | PF |  | supported | R
50084 | A |  | supported | R
50085 | LLV |  | supported | R
50086 | LNV |  | supported | R
50087 | Hz |  | supported | R
50089 | TotWhInj |  | unimplemented | R
50093 | TotWhAbs |  | unimplemented | R
50097 | TotVarhInj |  | unimplemented | R
50101 | TotVarhAbs |  | unimplemented | R
50105 | TmpAmb |  | supported | R
50106 | TmpCab |  | unimplemented | R
50107 | TmpSnk |  | supported | R
50108 | TmpTrns |  | supported | R
50109 | TmpSw |  | unimplemented | R
50110 | TmpOt |  | unimplemented | R
50111 | WL1 |  | unimplemented | R
50112 | VAL1 |  | unimplemented | R
50113 | VarL1 |  | unimplemented | R
50114 | PFL1 |  | unimplemented | R
50115 | AL1 |  | unimplemented | R
50116 | VL1L2 |  | supported | R
50117 | VL1 |  | supported | R
50118 | TotWhInjL1 |  | unimplemented | R
50122 | TotWhAbsL1 |  | unimplemented | R
50126 | TotVarhInjL1 |  | unimplemented | R
50130 | TotVarhAbsL1 |  | unimplemented | R
50134 | WL2 |  | unimplemented | R
50135 | VAL2 |  | unimplemented | R
50136 | VarL2 |  | unimplemented | R
50137 | PFL2 |  | unimplemented | R
50138 | AL2 |  | unimplemented | R
50139 | VL2L3 |  | unimplemented | R
50140 | VL2 |  | supported | R
50141 | TotWhInjL2 |  | unimplemented | R
50145 | TotWhAbsL2 |  | unimplemented | R
50149 | TotVarhInjL2 |  | unimplemented | R
50153 | TotVarhAbsL2 |  | unimplemented | R
50157 | WL3 |  | unimplemented | R
50158 | VAL3 |  | unimplemented | R
50159 | VarL3 |  | unimplemented | R
50160 | PFL3 |  | unimplemented | R
50161 | AL3 |  | unimplemented | R
50162 | VL3L1 |  | unimplemented | R
50163 | VL3 |  | unimplemented | R
50164 | TotWhInjL3 |  | unimplemented | R
50168 | TotWhAbsL3 |  | unimplemented | R
50172 | TotVarhInjL3 |  | unimplemented | R
50176 | TotVarhAbsL3 |  | unimplemented | R
50180 | ThrotPct |  | unimplemented | R
50181 | ThrotSrc |  | unimplemented | R
|  | MAX_W | unimplemented
|  | FIXED_W | unimplemented
|  | FIXED_VAR | unimplemented
|  | FIXED_PF | unimplemented
|  | VOLT_VAR | unimplemented
|  | FREQ_WATT | unimplemented
|  | DYN_REACT_CURR | unimplemented
|  | LVRT | unimplemented
|  | HVRT | unimplemented
|  | WATT_VAR | unimplemented
|  | VOLT_WATT | unimplemented
|  | SCHEDULED | unimplemented
|  | LFRT | unimplemented
|  | HFRT | unimplemented
|  | DERATED | unimplemented
50183 | A_SF |  | -2 | R
50184 | V_SF |  | -1 | R
50185 | Hz_SF |  | -2 | R
50186 | W_SF |  | 0 | R
50187 | PF_SF |  | -3 | R
50188 | VA_SF |  | 0 | R
50189 | Var_SF |  | 0 | R
50190 | TotWh_SF |  | 0 | R
50191 | TotVarh_SF |  | 0 | R
50192 | Tmp_SF |  | 0 | R
50193 | MnAlrmInfo |  | unimplemented | R

## 702
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50225 | ID |  | 702 | R
50226 | L |  | 50 | R
50227 | WMaxRtg |  | 5000 | R
50228 | WOvrExtRtg |  | 5000 | R
50229 | WOvrExtRtgPF |  | 100 | R
50230 | WUndExtRtg |  | 5000 | R
50231 | WUndExtRtgPF |  | 100 | R
50232 | VAMaxRtg |  | 5000 | R
50233 | VarMaxInjRtg |  | 3000 | R
50234 | VarMaxAbsRtg |  | 3000 | R
50235 | WChaRteMaxRtg |  | 5000 | R
50236 | WDisChaRteMaxRtg |  | 5000 | R
50237 | VAChaRteMaxRtg |  | 5000 | R
50238 | VADisChaRteMaxRtg |  | 5000 | R
50239 | VNomRtg |  | 2400 | R
50240 | VMaxRtg |  | 2640 | R
50241 | VMinRtg |  | 2112 | R
50242 | AMaxRtg |  | 20 | R
50243 | PFOvrExtRtg |  | unimplemented | R
50244 | PFUndExtRtg |  | unimplemented | R
50245 | ReactSusceptRtg |  | 0 | R
50246 | NorOpCatRtg |  | 1 | R
|  | CAT_A | supported
|  | CAT_B | supported
50247 | AbnOpCatRtg |  | 2 | R
|  | CAT_1 | supported
|  | CAT_2 | supported
|  | CAT_3 | supported
50248 | CtrlModes |  | 14239 | R
|  | MAX_W | supported
|  | FIXED_W | supported
|  | FIXED_VAR | supported
|  | FIXED_PF | supported
|  | VOLT_VAR | supported
|  | FREQ_WATT | supported
|  | DYN_REACT_CURR | supported
|  | LV_TRIP | supported
|  | HV_TRIP | supported
|  | WATT_VAR | supported
|  | VOLT_WATT | supported
|  | SCHEDULED | supported
|  | LF_TRIP | supported
|  | HF_TRIP | supported
50250 | IntIslandCatRtg |  | unimplemented | R
|  | UNCATEGORIZED | unimplemented
|  | INT_ISL_CAPABLE | unimplemented
|  | BLACK_START_CAPABLE | unimplemented
|  | ISOCH_CAPABLE | unimplemented
50251 | WMax |  | unimplemented | RW
50252 | WMaxOvrExt |  | unimplemented | RW
50253 | WOvrExtPF |  | unimplemented | RW
50254 | WMaxUndExt |  | unimplemented | RW
50255 | WUndExtPF |  | unimplemented | RW
50256 | VAMax |  | unimplemented | RW
50257 | VarMaxInj |  | unimplemented | RW
50258 | VarMaxAbs |  | unimplemented | RW
50259 | WChaRteMax |  | unimplemented | RW
50260 | WDisChaRteMax |  | unimplemented | RW
50261 | VAChaRteMax |  | unimplemented | RW
50262 | VADisChaRteMax |  | unimplemented | RW
50263 | VNom |  | unimplemented | RW
50264 | VMax |  | unimplemented | RW
50265 | VMin |  | unimplemented | RW
50266 | AMax |  | unimplemented | RW
50267 | PFOvrExt |  | unimplemented | RW
50268 | PFUndExt |  | unimplemented | RW
50269 | IntIslandCat |  | unimplemented | RW
|  | UNCATEGORIZED | unimplemented
|  | INT_ISL_CAPABLE | unimplemented
|  | BLACK_START_CAPABLE | unimplemented
|  | ISOCH_CAPABLE | unimplemented
50270 | W_SF |  | 0 | R
50271 | PF_SF |  | -2 | R
50272 | VA_SF |  | 0 | R
50273 | Var_SF |  | 0 | R
50274 | V_SF |  | -1 | R
50275 | A_SF |  | 0 | R
50276 | S_SF |  | 0 | R

## 703
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50277 | ID |  | 703 | R
50278 | L |  | 17 | R
50279 | ES |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50280 | ESVHi |  | supported | RW | 105 | 106
50281 | ESVLo |  | supported | RW | 88 | 95
50282 | ESHzHi |  | supported | RW | 60.1 | 61
50284 | ESHzLo |  | supported | RW | 59 | 59.9
50286 | ESDlyTms |  | supported | RW | 0 | 600
50288 | ESRndTms |  | unimplemented | RW
50290 | ESRmpTms |  | unimplemented | RW
50292 | ESDlyRemTms |  | supported | R | 0 | 600
50294 | V_SF |  | -1 | R
50295 | Hz_SF |  | -2 | R

## 704
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50296 | ID |  | 704 | R
50297 | L |  | 65 | R
50298 | PFWInjEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50299 | PFWInjEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50300 | PFWInjRvrtTms |  | unimplemented | RW
50302 | PFWInjRvrtRem |  | unimplemented | R
50304 | PFWAbsEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50305 | PFWAbsEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50306 | PFWAbsRvrtTms |  | unimplemented | RW
50308 | PFWAbsRvrtRem |  | unimplemented | R
50310 | WMaxLimPctEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50311 | WMaxLimPct |  | supported | RW | 0 | 100
50312 | WMaxLimPctRvrt |  | unimplemented | RW
50313 | WMaxLimPctEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50314 | WMaxLimPctRvrtTms |  | unimplemented | RW
50316 | WMaxLimPctRvrtRem |  | unimplemented | R
50318 | WSetEna |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50319 | WSetMod |  | unimplemented | RW
|  | W_MAX_PCT | unimplemented
|  | WATTS | unimplemented
50320 | WSet |  | unimplemented | RW
50322 | WSetRvrt |  | unimplemented | RW
50324 | WSetPct |  | unimplemented | RW
50325 | WSetPctRvrt |  | unimplemented | RW
50326 | WSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50327 | WSetRvrtTms |  | unimplemented | RW
50329 | WSetRvrtRem |  | unimplemented | R
50331 | VarSetEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50332 | VarSetMod |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | supported
|  | VAR_AVAIL_PCT | supported
|  | VA_MAX_PCT | supported
|  | VARS | supported
50333 | VarSetPri |  | supported | RW
|  | ACTIVE | supported
|  | REACTIVE | supported
|  | VENDOR | supported
50334 | VarSet |  | unimplemented | RW
50336 | VarSetRvrt |  | unimplemented | RW
50338 | VarSetPct |  | supported | RW | -100 | 100
50339 | VarSetPctRvrt |  | unimplemented | RW
50340 | VarSetEnaRvrt |  | unimplemented | RW
|  | DISABLED | unimplemented
|  | ENABLED | unimplemented
50341 | VarSetRvrtTms |  | unimplemented | RW
50343 | VarSetRvrtRem |  | unimplemented | R
50345 | WRmp |  | supported | RW | 0 | 100
50346 | WRmpRef |  | supported | RW
|  | A_MAX | supported
|  | W_MAX | supported
50347 | VarRmp |  | unimplemented | RW
50348 | AntiIslEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50349 | PF_SF |  | -3 | R
50350 | WMaxLimPct_SF |  | 0 | R
50351 | WSet_SF |  | 0 | R
50352 | WSetPct_SF |  | -1 | R
50353 | VarSet_SF |  | -1 | R
50354 | VarSetPct_SF |  | 0 | R
50355 | PFWInj.PF |  | supported | RW | 0.85 | 1
50356 | PFWInj.Ext |  | supported | RW
|  | OVER_EXCITED | supported
|  | UNDER_EXCITED | supported
50357 | PFWInjRvrt.PF |  | unimplemented | RW
50358 | PFWInjRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
50359 | PFWAbs.PF |  | unimplemented | RW
50360 | PFWAbs.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented
50361 | PFWAbsRvrt.PF |  | unimplemented | RW
50362 | PFWAbsRvrt.Ext |  | unimplemented | RW
|  | OVER_EXCITED | unimplemented
|  | UNDER_EXCITED | unimplemented

## 705
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50363 | ID |  | 705 | R
50364 | L |  | 49 | R
50365 | Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50366 | AdptCrvReq |  | supported | RW
50367 | AdptCrvRslt |  | supported | R
|  | IN_PROGRESS | supported
|  | COMPLETED | supported
|  | FAILED | supported
50368 | NPt |  | 4 | R
50369 | NCrv |  | 2 | R
50370 | RvrtTms |  | unimplemented | RW
50372 | RvrtRem |  | unimplemented | R
50374 | RvrtCrv |  | unimplemented | RW
50375 | V_SF |  | -1 | R
50376 | DeptRef_SF |  | 0 | R
50377 | RspTms_SF |  | -2 | R
50378 | Crv.1.ActPt |  | supported | RW | 4 | 4
50379 | Crv.1.DeptRef |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | supported
|  | VAR_AVAL_PCT | supported
|  | VA_MAX_PCT | supported
50380 | Crv.1.Pri |  | supported | RW
|  | ACTIVE | supported
|  | REACTIVE | supported
|  | VENDOR | supported
50381 | Crv.1.VRef |  | supported | RW | 95 | 105
50382 | Crv.1.VRefAuto |  | supported | R
50383 | Crv.1.VRefAutoEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50384 | Crv.1.VRefAutoTms |  | supported | RW | 300 | 5000
50385 | Crv.1.RspTms |  | supported | RW | 1 | 90
50387 | Crv.1.ReadOnly |  | 1 | R
|  | RW | supported
|  | R | supported
50388 | Crv.1.Pt.1.V |  | supported | RW | 77 | 98
50389 | Crv.1.Pt.1.Var |  | supported | RW | 0 | 100
50390 | Crv.1.Pt.2.V |  | supported | RW | 97 | 100
50391 | Crv.1.Pt.2.Var |  | supported | RW | 0 | 0
50392 | Crv.1.Pt.3.V |  | supported | RW | 100 | 103
50393 | Crv.1.Pt.3.Var |  | supported | RW | 0 | 0
50394 | Crv.1.Pt.4.V |  | supported | RW | 102 | 118
50395 | Crv.1.Pt.4.Var |  | supported | RW | -100 | 0
50396 | Crv.2.ActPt |  | supported | RW
50397 | Crv.2.DeptRef |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | supported
|  | VAR_AVAL_PCT | supported
|  | VA_MAX_PCT | supported
50398 | Crv.2.Pri |  | supported | RW
|  | ACTIVE | supported
|  | REACTIVE | supported
|  | VENDOR | supported
50399 | Crv.2.VRef |  | supported | RW
50400 | Crv.2.VRefAuto |  | supported | R
50401 | Crv.2.VRefAutoEna |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50402 | Crv.2.VRefAutoTms |  | supported | RW
50403 | Crv.2.RspTms |  | supported | RW
50405 | Crv.2.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
50406 | Crv.2.Pt.1.V |  | supported | RW
50407 | Crv.2.Pt.1.Var |  | supported | RW
50408 | Crv.2.Pt.2.V |  | supported | RW
50409 | Crv.2.Pt.2.Var |  | supported | RW
50410 | Crv.2.Pt.3.V |  | supported | RW
50411 | Crv.2.Pt.3.Var |  | supported | RW
50412 | Crv.2.Pt.4.V |  | supported | RW
50413 | Crv.2.Pt.4.Var |  | supported | RW

## 706
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50414 | ID |  | 706 | R
50415 | L |  | 31 | R
50416 | Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50417 | AdptCrvReq |  | supported | RW
50418 | AdptCrvRslt |  | supported | R
|  | IN_PROGRESS | supported
|  | COMPLETED | supported
|  | FAILED | supported
50419 | NPt |  | 2 | R
50420 | NCrv |  | 2 | R
50421 | RvrtTms |  | unimplemented | RW
50423 | RvrtRem |  | unimplemented | R
50425 | RvrtCrv |  | unimplemented | RW
50426 | V_SF |  | -1 | R
50427 | DeptRef_SF |  | 0 | R
50428 | RspTms_SF |  | -2 | R
50429 | Crv.1.ActPt |  | supported | RW | 2 | 2
50430 | Crv.1.DeptRef |  | supported | RW
|  | W_MAX_PCT | supported
|  | W_AVAL_PCT | supported
50431 | Crv.1.RspTms |  | supported | RW | 0.5 | 60
50433 | Crv.1.ReadOnly |  | 1 | R
|  | RW | supported
|  | R | supported
50434 | Crv.1.Pt.1.V |  | supported | RW | 105 | 109
50435 | Crv.1.Pt.1.W |  | supported | RW | 100 | 100
50436 | Crv.1.Pt.2.V |  | supported | RW | 107 | 110
50437 | Crv.1.Pt.2.W |  | supported | RW | 0 | 100
50438 | Crv.2.ActPt |  | supported | RW
50439 | Crv.2.DeptRef |  | supported | RW
|  | W_MAX_PCT | supported
|  | W_AVAL_PCT | supported
50440 | Crv.2.RspTms |  | supported | RW
50442 | Crv.2.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
50443 | Crv.2.Pt.1.V |  | supported | RW
50444 | Crv.2.Pt.1.W |  | supported | RW
50445 | Crv.2.Pt.2.V |  | supported | RW
50446 | Crv.2.Pt.2.W |  | supported | RW

## 707
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50447 | ID |  | 707 | R
50448 | L |  | 105 | R
50449 | Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50450 | AdptCrvReq |  | supported | RW
50451 | AdptCrvRslt |  | supported | R
|  | IN_PROGRESS | supported
|  | COMPLETED | supported
|  | FAILED | supported
50452 | NPt |  | 5 | R
50453 | NCrvSet |  | 2 | R
50454 | V_SF |  | -1 | R
50455 | Tms_SF |  | -2 | R
50456 | Crv.1.ReadOnly |  | 1 | R
|  | RW | supported
|  | R | supported
50457 | Crv.1.MustTrip.ActPt |  | supported | RW | 5 | 5
50458 | Crv.1.MustTrip.Pt.1.V |  | supported | RW | 0 | 50
50459 | Crv.1.MustTrip.Pt.1.Tms |  | supported | RW | 2 | 21
50461 | Crv.1.MustTrip.Pt.2.V |  | supported | RW | 0 | 50
50462 | Crv.1.MustTrip.Pt.2.Tms |  | supported | RW | 2 | 21
50464 | Crv.1.MustTrip.Pt.3.V |  | supported | RW | 0 | 50
50465 | Crv.1.MustTrip.Pt.3.Tms |  | supported | RW | 21 | 50
50467 | Crv.1.MustTrip.Pt.4.V |  | supported | RW | 0 | 88
50468 | Crv.1.MustTrip.Pt.4.Tms |  | supported | RW | 21 | 50
50470 | Crv.1.MustTrip.Pt.5.V |  | supported | RW | 0 | 88
50471 | Crv.1.MustTrip.Pt.5.Tms |  | supported | RW | 21 | 51
50473 | Crv.1.MayTrip.ActPt |  | unimplemented | RW
50474 | Crv.1.MayTrip.Pt.1.V |  | unimplemented | RW
50475 | Crv.1.MayTrip.Pt.1.Tms |  | unimplemented | RW
50477 | Crv.1.MayTrip.Pt.2.V |  | unimplemented | RW
50478 | Crv.1.MayTrip.Pt.2.Tms |  | unimplemented | RW
50480 | Crv.1.MayTrip.Pt.3.V |  | unimplemented | RW
50481 | Crv.1.MayTrip.Pt.3.Tms |  | unimplemented | RW
50483 | Crv.1.MayTrip.Pt.4.V |  | unimplemented | RW
50484 | Crv.1.MayTrip.Pt.4.Tms |  | unimplemented | RW
50486 | Crv.1.MayTrip.Pt.5.V |  | unimplemented | RW
50487 | Crv.1.MayTrip.Pt.5.Tms |  | unimplemented | RW
50489 | Crv.1.MomCess.ActPt |  | unimplemented | RW
50490 | Crv.1.MomCess.Pt.1.V |  | unimplemented | RW
50491 | Crv.1.MomCess.Pt.1.Tms |  | unimplemented | RW
50493 | Crv.1.MomCess.Pt.2.V |  | unimplemented | RW
50494 | Crv.1.MomCess.Pt.2.Tms |  | unimplemented | RW
50496 | Crv.1.MomCess.Pt.3.V |  | unimplemented | RW
50497 | Crv.1.MomCess.Pt.3.Tms |  | unimplemented | RW
50499 | Crv.1.MomCess.Pt.4.V |  | unimplemented | RW
50500 | Crv.1.MomCess.Pt.4.Tms |  | unimplemented | RW
50502 | Crv.1.MomCess.Pt.5.V |  | unimplemented | RW
50503 | Crv.1.MomCess.Pt.5.Tms |  | unimplemented | RW
50505 | Crv.2.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
50506 | Crv.2.MustTrip.ActPt |  | supported | RW
50507 | Crv.2.MustTrip.Pt.1.V |  | supported | RW
50508 | Crv.2.MustTrip.Pt.1.Tms |  | supported | RW
50510 | Crv.2.MustTrip.Pt.2.V |  | supported | RW
50511 | Crv.2.MustTrip.Pt.2.Tms |  | supported | RW
50513 | Crv.2.MustTrip.Pt.3.V |  | supported | RW
50514 | Crv.2.MustTrip.Pt.3.Tms |  | supported | RW
50516 | Crv.2.MustTrip.Pt.4.V |  | supported | RW
50517 | Crv.2.MustTrip.Pt.4.Tms |  | supported | RW
50519 | Crv.2.MustTrip.Pt.5.V |  | supported | RW
50520 | Crv.2.MustTrip.Pt.5.Tms |  | supported | RW
50522 | Crv.2.MayTrip.ActPt |  | unimplemented | RW
50523 | Crv.2.MayTrip.Pt.1.V |  | unimplemented | RW
50524 | Crv.2.MayTrip.Pt.1.Tms |  | unimplemented | RW
50526 | Crv.2.MayTrip.Pt.2.V |  | unimplemented | RW
50527 | Crv.2.MayTrip.Pt.2.Tms |  | unimplemented | RW
50529 | Crv.2.MayTrip.Pt.3.V |  | unimplemented | RW
50530 | Crv.2.MayTrip.Pt.3.Tms |  | unimplemented | RW
50532 | Crv.2.MayTrip.Pt.4.V |  | unimplemented | RW
50533 | Crv.2.MayTrip.Pt.4.Tms |  | unimplemented | RW
50535 | Crv.2.MayTrip.Pt.5.V |  | unimplemented | RW
50536 | Crv.2.MayTrip.Pt.5.Tms |  | unimplemented | RW
50538 | Crv.2.MomCess.ActPt |  | unimplemented | RW
50539 | Crv.2.MomCess.Pt.1.V |  | unimplemented | RW
50540 | Crv.2.MomCess.Pt.1.Tms |  | unimplemented | RW
50542 | Crv.2.MomCess.Pt.2.V |  | unimplemented | RW
50543 | Crv.2.MomCess.Pt.2.Tms |  | unimplemented | RW
50545 | Crv.2.MomCess.Pt.3.V |  | unimplemented | RW
50546 | Crv.2.MomCess.Pt.3.Tms |  | unimplemented | RW
50548 | Crv.2.MomCess.Pt.4.V |  | unimplemented | RW
50549 | Crv.2.MomCess.Pt.4.Tms |  | unimplemented | RW
50551 | Crv.2.MomCess.Pt.5.V |  | unimplemented | RW
50552 | Crv.2.MomCess.Pt.5.Tms |  | unimplemented | RW

## 708
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50554 | ID |  | 708 | R
50555 | L |  | 105 | R
50556 | Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50557 | AdptCrvReq |  | supported | RW
50558 | AdptCrvRslt |  | supported | R
|  | IN_PROGRESS | supported
|  | COMPLETED | supported
|  | FAILED | supported
50559 | NPt |  | 5 | R
50560 | NCrvSet |  | 2 | R
50561 | V_SF |  | -1 | R
50562 | Tms_SF |  | -2 | R
50563 | Crv.1.ReadOnly |  | 1 | R
|  | RW | supported
|  | R | supported
50564 | Crv.1.MustTrip.ActPt |  | supported | RW | 5 | 5
50565 | Crv.1.MustTrip.Pt.1.V |  | supported | RW | 0 | 50
50566 | Crv.1.MustTrip.Pt.1.Tms |  | supported | RW | 0.16 | 0.16
50568 | Crv.1.MustTrip.Pt.2.V |  | supported | RW | 120 | 120
50569 | Crv.1.MustTrip.Pt.2.Tms |  | supported | RW | 0.16 | 0.16
50571 | Crv.1.MustTrip.Pt.3.V |  | supported | RW | 120 | 120
50572 | Crv.1.MustTrip.Pt.3.Tms |  | supported | RW | 1 | 13
50574 | Crv.1.MustTrip.Pt.4.V |  | supported | RW | 110 | 120
50575 | Crv.1.MustTrip.Pt.4.Tms |  | supported | RW | 1 | 13
50577 | Crv.1.MustTrip.Pt.5.V |  | supported | RW | 110 | 120
50578 | Crv.1.MustTrip.Pt.5.Tms |  | supported | RW | 2 | 14
50580 | Crv.1.MayTrip.ActPt |  | unimplemented | RW
50581 | Crv.1.MayTrip.Pt.1.V |  | unimplemented | RW
50582 | Crv.1.MayTrip.Pt.1.Tms |  | unimplemented | RW
50584 | Crv.1.MayTrip.Pt.2.V |  | unimplemented | RW
50585 | Crv.1.MayTrip.Pt.2.Tms |  | unimplemented | RW
50587 | Crv.1.MayTrip.Pt.3.V |  | unimplemented | RW
50588 | Crv.1.MayTrip.Pt.3.Tms |  | unimplemented | RW
50590 | Crv.1.MayTrip.Pt.4.V |  | unimplemented | RW
50591 | Crv.1.MayTrip.Pt.4.Tms |  | unimplemented | RW
50593 | Crv.1.MayTrip.Pt.5.V |  | unimplemented | RW
50594 | Crv.1.MayTrip.Pt.5.Tms |  | unimplemented | RW
50596 | Crv.1.MomCess.ActPt |  | unimplemented | RW
50597 | Crv.1.MomCess.Pt.1.V |  | unimplemented | RW
50598 | Crv.1.MomCess.Pt.1.Tms |  | unimplemented | RW
50600 | Crv.1.MomCess.Pt.2.V |  | unimplemented | RW
50601 | Crv.1.MomCess.Pt.2.Tms |  | unimplemented | RW
50603 | Crv.1.MomCess.Pt.3.V |  | unimplemented | RW
50604 | Crv.1.MomCess.Pt.3.Tms |  | unimplemented | RW
50606 | Crv.1.MomCess.Pt.4.V |  | unimplemented | RW
50607 | Crv.1.MomCess.Pt.4.Tms |  | unimplemented | RW
50609 | Crv.1.MomCess.Pt.5.V |  | unimplemented | RW
50610 | Crv.1.MomCess.Pt.5.Tms |  | unimplemented | RW
50612 | Crv.2.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
50613 | Crv.2.MustTrip.ActPt |  | supported | RW
50614 | Crv.2.MustTrip.Pt.1.V |  | supported | RW
50615 | Crv.2.MustTrip.Pt.1.Tms |  | supported | RW
50617 | Crv.2.MustTrip.Pt.2.V |  | supported | RW
50618 | Crv.2.MustTrip.Pt.2.Tms |  | supported | RW
50620 | Crv.2.MustTrip.Pt.3.V |  | supported | RW
50621 | Crv.2.MustTrip.Pt.3.Tms |  | supported | RW
50623 | Crv.2.MustTrip.Pt.4.V |  | supported | RW
50624 | Crv.2.MustTrip.Pt.4.Tms |  | supported | RW
50626 | Crv.2.MustTrip.Pt.5.V |  | supported | RW
50627 | Crv.2.MustTrip.Pt.5.Tms |  | supported | RW
50629 | Crv.2.MayTrip.ActPt |  | unimplemented | RW
50630 | Crv.2.MayTrip.Pt.1.V |  | unimplemented | RW
50631 | Crv.2.MayTrip.Pt.1.Tms |  | unimplemented | RW
50633 | Crv.2.MayTrip.Pt.2.V |  | unimplemented | RW
50634 | Crv.2.MayTrip.Pt.2.Tms |  | unimplemented | RW
50636 | Crv.2.MayTrip.Pt.3.V |  | unimplemented | RW
50637 | Crv.2.MayTrip.Pt.3.Tms |  | unimplemented | RW
50639 | Crv.2.MayTrip.Pt.4.V |  | unimplemented | RW
50640 | Crv.2.MayTrip.Pt.4.Tms |  | unimplemented | RW
50642 | Crv.2.MayTrip.Pt.5.V |  | unimplemented | RW
50643 | Crv.2.MayTrip.Pt.5.Tms |  | unimplemented | RW
50645 | Crv.2.MomCess.ActPt |  | unimplemented | RW
50646 | Crv.2.MomCess.Pt.1.V |  | unimplemented | RW
50647 | Crv.2.MomCess.Pt.1.Tms |  | unimplemented | RW
50649 | Crv.2.MomCess.Pt.2.V |  | unimplemented | RW
50650 | Crv.2.MomCess.Pt.2.Tms |  | unimplemented | RW
50652 | Crv.2.MomCess.Pt.3.V |  | unimplemented | RW
50653 | Crv.2.MomCess.Pt.3.Tms |  | unimplemented | RW
50655 | Crv.2.MomCess.Pt.4.V |  | unimplemented | RW
50656 | Crv.2.MomCess.Pt.4.Tms |  | unimplemented | RW
50658 | Crv.2.MomCess.Pt.5.V |  | unimplemented | RW
50659 | Crv.2.MomCess.Pt.5.Tms |  | unimplemented | RW

## 709
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50661 | ID |  | 709 | R
50662 | L |  | 135 | R
50663 | Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50664 | AdptCrvReq |  | supported | RW
50665 | AdptCrvRslt |  | supported | R
|  | IN_PROGRESS | supported
|  | COMPLETED | supported
|  | FAILED | supported
50666 | NPt |  | 5 | R
50667 | NCrvSet |  | 2 | R
50668 | Hz_SF |  | -2 | R
50669 | Tms_SF |  | -2 | R
50670 | Crv.1.ReadOnly |  | 1 | R
|  | RW | supported
|  | R | supported
50671 | Crv.1.MustTrip.ActPt |  | supported | RW | 5 | 5
50672 | Crv.1.MustTrip.Pt.1.Hz |  | supported | RW | 0 | 50
50674 | Crv.1.MustTrip.Pt.1.Tms |  | supported | RW | 0.16 | 100
50676 | Crv.1.MustTrip.Pt.2.Hz |  | supported | RW | 50 | 57
50678 | Crv.1.MustTrip.Pt.2.Tms |  | supported | RW | 0.16 | 100
50680 | Crv.1.MustTrip.Pt.3.Hz |  | supported | RW | 50 | 57
50682 | Crv.1.MustTrip.Pt.3.Tms |  | supported | RW | 180 | 100
50684 | Crv.1.MustTrip.Pt.4.Hz |  | supported | RW | 50 | 59
50686 | Crv.1.MustTrip.Pt.4.Tms |  | supported | RW | 180 | 100
50688 | Crv.1.MustTrip.Pt.5.Hz |  | supported | RW | 50 | 59
50690 | Crv.1.MustTrip.Pt.5.Tms |  | supported | RW | 180 | 100
50692 | Crv.1.MayTrip.ActPt |  | unimplemented | RW
50693 | Crv.1.MayTrip.Pt.1.Hz |  | unimplemented | RW
50695 | Crv.1.MayTrip.Pt.1.Tms |  | unimplemented | RW
50697 | Crv.1.MayTrip.Pt.2.Hz |  | unimplemented | RW
50699 | Crv.1.MayTrip.Pt.2.Tms |  | unimplemented | RW
50701 | Crv.1.MayTrip.Pt.3.Hz |  | unimplemented | RW
50703 | Crv.1.MayTrip.Pt.3.Tms |  | unimplemented | RW
50705 | Crv.1.MayTrip.Pt.4.Hz |  | unimplemented | RW
50707 | Crv.1.MayTrip.Pt.4.Tms |  | unimplemented | RW
50709 | Crv.1.MayTrip.Pt.5.Hz |  | unimplemented | RW
50711 | Crv.1.MayTrip.Pt.5.Tms |  | unimplemented | RW
50713 | Crv.1.MomCess.ActPt |  | unimplemented | RW
50714 | Crv.1.MomCess.Pt.1.Hz |  | unimplemented | RW
50716 | Crv.1.MomCess.Pt.1.Tms |  | unimplemented | RW
50718 | Crv.1.MomCess.Pt.2.Hz |  | unimplemented | RW
50720 | Crv.1.MomCess.Pt.2.Tms |  | unimplemented | RW
50722 | Crv.1.MomCess.Pt.3.Hz |  | unimplemented | RW
50724 | Crv.1.MomCess.Pt.3.Tms |  | unimplemented | RW
50726 | Crv.1.MomCess.Pt.4.Hz |  | unimplemented | RW
50728 | Crv.1.MomCess.Pt.4.Tms |  | unimplemented | RW
50730 | Crv.1.MomCess.Pt.5.Hz |  | unimplemented | RW
50732 | Crv.1.MomCess.Pt.5.Tms |  | unimplemented | RW
50734 | Crv.2.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
50735 | Crv.2.MustTrip.ActPt |  | supported | RW
50736 | Crv.2.MustTrip.Pt.1.Hz |  | supported | RW
50738 | Crv.2.MustTrip.Pt.1.Tms |  | supported | RW
50740 | Crv.2.MustTrip.Pt.2.Hz |  | supported | RW
50742 | Crv.2.MustTrip.Pt.2.Tms |  | supported | RW
50744 | Crv.2.MustTrip.Pt.3.Hz |  | supported | RW
50746 | Crv.2.MustTrip.Pt.3.Tms |  | supported | RW
50748 | Crv.2.MustTrip.Pt.4.Hz |  | supported | RW
50750 | Crv.2.MustTrip.Pt.4.Tms |  | supported | RW
50752 | Crv.2.MustTrip.Pt.5.Hz |  | supported | RW
50754 | Crv.2.MustTrip.Pt.5.Tms |  | supported | RW
50756 | Crv.2.MayTrip.ActPt |  | unimplemented | RW
50757 | Crv.2.MayTrip.Pt.1.Hz |  | unimplemented | RW
50759 | Crv.2.MayTrip.Pt.1.Tms |  | unimplemented | RW
50761 | Crv.2.MayTrip.Pt.2.Hz |  | unimplemented | RW
50763 | Crv.2.MayTrip.Pt.2.Tms |  | unimplemented | RW
50765 | Crv.2.MayTrip.Pt.3.Hz |  | unimplemented | RW
50767 | Crv.2.MayTrip.Pt.3.Tms |  | unimplemented | RW
50769 | Crv.2.MayTrip.Pt.4.Hz |  | unimplemented | RW
50771 | Crv.2.MayTrip.Pt.4.Tms |  | unimplemented | RW
50773 | Crv.2.MayTrip.Pt.5.Hz |  | unimplemented | RW
50775 | Crv.2.MayTrip.Pt.5.Tms |  | unimplemented | RW
50777 | Crv.2.MomCess.ActPt |  | unimplemented | RW
50778 | Crv.2.MomCess.Pt.1.Hz |  | unimplemented | RW
50780 | Crv.2.MomCess.Pt.1.Tms |  | unimplemented | RW
50782 | Crv.2.MomCess.Pt.2.Hz |  | unimplemented | RW
50784 | Crv.2.MomCess.Pt.2.Tms |  | unimplemented | RW
50786 | Crv.2.MomCess.Pt.3.Hz |  | unimplemented | RW
50788 | Crv.2.MomCess.Pt.3.Tms |  | unimplemented | RW
50790 | Crv.2.MomCess.Pt.4.Hz |  | unimplemented | RW
50792 | Crv.2.MomCess.Pt.4.Tms |  | unimplemented | RW
50794 | Crv.2.MomCess.Pt.5.Hz |  | unimplemented | RW
50796 | Crv.2.MomCess.Pt.5.Tms |  | unimplemented | RW

## 710
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50798 | ID |  | 710 | R
50799 | L |  | 135 | R
50800 | Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50801 | AdptCrvReq |  | supported | RW
50802 | AdptCrvRslt |  | supported | R
|  | IN_PROGRESS | supported
|  | COMPLETED | supported
|  | FAILED | supported
50803 | NPt |  | 5 | R
50804 | NCrvSet |  | 2 | R
50805 | Hz_SF |  | -2 | R
50806 | Tms_SF |  | -2 | R
50807 | Crv.1.ReadOnly |  | 1 | R
|  | RW | supported
|  | R | supported
50808 | Crv.1.MustTrip.ActPt |  | supported | RW | 5 | 5
50809 | Crv.1.MustTrip.Pt.1.Hz |  | supported | RW | 62 | 67
50811 | Crv.1.MustTrip.Pt.1.Tms |  | supported | RW | 0.16 | 100
50813 | Crv.1.MustTrip.Pt.2.Hz |  | supported | RW | 61.8 | 66
50815 | Crv.1.MustTrip.Pt.2.Tms |  | supported | RW | 0.16 | 100
50817 | Crv.1.MustTrip.Pt.3.Hz |  | supported | RW | 61.8 | 66
50819 | Crv.1.MustTrip.Pt.3.Tms |  | supported | RW | 180 | 100
50821 | Crv.1.MustTrip.Pt.4.Hz |  | supported | RW | 61 | 66
50823 | Crv.1.MustTrip.Pt.4.Tms |  | supported | RW | 180 | 100
50825 | Crv.1.MustTrip.Pt.5.Hz |  | supported | RW | 61 | 66
50827 | Crv.1.MustTrip.Pt.5.Tms |  | supported | RW | 180 | 100
50829 | Crv.1.MayTrip.ActPt |  | unimplemented | RW
50830 | Crv.1.MayTrip.Pt.1.Hz |  | unimplemented | RW
50832 | Crv.1.MayTrip.Pt.1.Tms |  | unimplemented | RW
50834 | Crv.1.MayTrip.Pt.2.Hz |  | unimplemented | RW
50836 | Crv.1.MayTrip.Pt.2.Tms |  | unimplemented | RW
50838 | Crv.1.MayTrip.Pt.3.Hz |  | unimplemented | RW
50840 | Crv.1.MayTrip.Pt.3.Tms |  | unimplemented | RW
50842 | Crv.1.MayTrip.Pt.4.Hz |  | unimplemented | RW
50844 | Crv.1.MayTrip.Pt.4.Tms |  | unimplemented | RW
50846 | Crv.1.MayTrip.Pt.5.Hz |  | unimplemented | RW
50848 | Crv.1.MayTrip.Pt.5.Tms |  | unimplemented | RW
50850 | Crv.1.MomCess.ActPt |  | unimplemented | RW
50851 | Crv.1.MomCess.Pt.1.Hz |  | unimplemented | RW
50853 | Crv.1.MomCess.Pt.1.Tms |  | unimplemented | RW
50855 | Crv.1.MomCess.Pt.2.Hz |  | unimplemented | RW
50857 | Crv.1.MomCess.Pt.2.Tms |  | unimplemented | RW
50859 | Crv.1.MomCess.Pt.3.Hz |  | unimplemented | RW
50861 | Crv.1.MomCess.Pt.3.Tms |  | unimplemented | RW
50863 | Crv.1.MomCess.Pt.4.Hz |  | unimplemented | RW
50865 | Crv.1.MomCess.Pt.4.Tms |  | unimplemented | RW
50867 | Crv.1.MomCess.Pt.5.Hz |  | unimplemented | RW
50869 | Crv.1.MomCess.Pt.5.Tms |  | unimplemented | RW
50871 | Crv.2.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
50872 | Crv.2.MustTrip.ActPt |  | supported | RW
50873 | Crv.2.MustTrip.Pt.1.Hz |  | supported | RW
50875 | Crv.2.MustTrip.Pt.1.Tms |  | supported | RW
50877 | Crv.2.MustTrip.Pt.2.Hz |  | supported | RW
50879 | Crv.2.MustTrip.Pt.2.Tms |  | supported | RW
50881 | Crv.2.MustTrip.Pt.3.Hz |  | supported | RW
50883 | Crv.2.MustTrip.Pt.3.Tms |  | supported | RW
50885 | Crv.2.MustTrip.Pt.4.Hz |  | supported | RW
50887 | Crv.2.MustTrip.Pt.4.Tms |  | supported | RW
50889 | Crv.2.MustTrip.Pt.5.Hz |  | supported | RW
50891 | Crv.2.MustTrip.Pt.5.Tms |  | supported | RW
50893 | Crv.2.MayTrip.ActPt |  | unimplemented | RW
50894 | Crv.2.MayTrip.Pt.1.Hz |  | unimplemented | RW
50896 | Crv.2.MayTrip.Pt.1.Tms |  | unimplemented | RW
50898 | Crv.2.MayTrip.Pt.2.Hz |  | unimplemented | RW
50900 | Crv.2.MayTrip.Pt.2.Tms |  | unimplemented | RW
50902 | Crv.2.MayTrip.Pt.3.Hz |  | unimplemented | RW
50904 | Crv.2.MayTrip.Pt.3.Tms |  | unimplemented | RW
50906 | Crv.2.MayTrip.Pt.4.Hz |  | unimplemented | RW
50908 | Crv.2.MayTrip.Pt.4.Tms |  | unimplemented | RW
50910 | Crv.2.MayTrip.Pt.5.Hz |  | unimplemented | RW
50912 | Crv.2.MayTrip.Pt.5.Tms |  | unimplemented | RW
50914 | Crv.2.MomCess.ActPt |  | unimplemented | RW
50915 | Crv.2.MomCess.Pt.1.Hz |  | unimplemented | RW
50917 | Crv.2.MomCess.Pt.1.Tms |  | unimplemented | RW
50919 | Crv.2.MomCess.Pt.2.Hz |  | unimplemented | RW
50921 | Crv.2.MomCess.Pt.2.Tms |  | unimplemented | RW
50923 | Crv.2.MomCess.Pt.3.Hz |  | unimplemented | RW
50925 | Crv.2.MomCess.Pt.3.Tms |  | unimplemented | RW
50927 | Crv.2.MomCess.Pt.4.Hz |  | unimplemented | RW
50929 | Crv.2.MomCess.Pt.4.Tms |  | unimplemented | RW
50931 | Crv.2.MomCess.Pt.5.Hz |  | unimplemented | RW
50933 | Crv.2.MomCess.Pt.5.Tms |  | unimplemented | RW

## 711
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50935 | ID |  | 711 | R
50936 | L |  | 32 | R
50937 | Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50938 | AdptCtlReq |  | supported | RW
50939 | AdptCtlRslt |  | supported | R
|  | IN_PROGRESS | supported
|  | COMPLETED | supported
|  | FAILED | supported
50940 | NCtl |  | 2 | R
50941 | RvrtTms |  | unimplemented | RW
50943 | RvrtRem |  | unimplemented | R
50945 | RvrtCtl |  | unimplemented | RW
50946 | Db_SF |  | -3 | R
50947 | K_SF |  | -2 | R
50948 | RspTms_SF |  | -2 | R
50949 | Ctl.1.DbOf |  | supported | RW | 0.017 | 1
50951 | Ctl.1.DbUf |  | supported | RW | 0.017 | 1
50953 | Ctl.1.KOf |  | supported | RW | 0.02 | 0.05
50954 | Ctl.1.KUf |  | supported | RW | 0.02 | 0.05
50955 | Ctl.1.RspTms |  | supported | RW | 0.2 | 10
50957 | Ctl.1.PMin |  | supported | RW | 0 | 100
50958 | Ctl.1.ReadOnly |  | 1 | R
|  | RW | supported
|  | R | supported
50959 | Ctl.2.DbOf |  | supported | RW
50961 | Ctl.2.DbUf |  | supported | RW
50963 | Ctl.2.KOf |  | supported | RW
50964 | Ctl.2.KUf |  | supported | RW
50965 | Ctl.2.RspTms |  | supported | RW
50967 | Ctl.2.PMin |  | supported | RW
50968 | Ctl.2.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported

## 712
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
50969 | ID |  | 712 | R
50970 | L |  | 44 | R
50971 | Ena |  | supported | RW
|  | DISABLED | supported
|  | ENABLED | supported
50972 | AdptCrvReq |  | supported | RW
50973 | AdptCrvRslt |  | supported | R
|  | IN_PROGRESS | supported
|  | COMPLETED | supported
|  | FAILED | supported
50974 | NPt |  | 6 | R
50975 | NCrv |  | 2 | R
50976 | RvrtTms |  | unimplemented | RW
50978 | RvrtRem |  | unimplemented | R
50980 | RvrtCrv |  | unimplemented | RW
50981 | W_SF |  | 0 | R
50982 | DeptRef_SF |  | 0 | R
50983 | Crv.1.ActPt |  | supported | RW | 6 | 6
50984 | Crv.1.DeptRef |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | supported
|  | VAR_AVAL_PCT | supported
|  | VA_MAX_PCT | supported
50985 | Crv.1.Pri |  | supported | RW
|  | ACTIVE | supported
|  | REACTIVE | supported
50986 | Crv.1.ReadOnly |  | 1 | R
|  | RW | supported
|  | R | supported
50987 | Crv.1.Pt.1.W |  | supported | RW | 0 | 100
50988 | Crv.1.Pt.1.Var |  | supported | RW | 0 | 80
50989 | Crv.1.Pt.2.W |  | supported | RW | 0 | 100
50990 | Crv.1.Pt.2.Var |  | supported | RW | 0 | 80
50991 | Crv.1.Pt.3.W |  | supported | RW | 0 | 100
50992 | Crv.1.Pt.3.Var |  | supported | RW | 0 | 80
50993 | Crv.1.Pt.4.W |  | supported | RW | -100 | 0
50994 | Crv.1.Pt.4.Var |  | supported | RW | -80 | 0
50995 | Crv.1.Pt.5.W |  | supported | RW | -100 | 0
50996 | Crv.1.Pt.5.Var |  | supported | RW | -80 | 0
50997 | Crv.1.Pt.6.W |  | supported | RW | -100 | 0
50998 | Crv.1.Pt.6.Var |  | supported | RW | -80 | 0
50999 | Crv.2.ActPt |  | supported | RW
51000 | Crv.2.DeptRef |  | supported | RW
|  | W_MAX_PCT | supported
|  | VAR_MAX_PCT | supported
|  | VAR_AVAL_PCT | supported
|  | VA_MAX_PCT | supported
51001 | Crv.2.Pri |  | supported | RW
|  | ACTIVE | supported
|  | REACTIVE | supported
51002 | Crv.2.ReadOnly |  | 0 | R
|  | RW | supported
|  | R | supported
51003 | Crv.2.Pt.1.W |  | supported | RW
51004 | Crv.2.Pt.1.Var |  | supported | RW
51005 | Crv.2.Pt.2.W |  | supported | RW
51006 | Crv.2.Pt.2.Var |  | supported | RW
51007 | Crv.2.Pt.3.W |  | supported | RW
51008 | Crv.2.Pt.3.Var |  | supported | RW
51009 | Crv.2.Pt.4.W |  | supported | RW
51010 | Crv.2.Pt.4.Var |  | supported | RW
51011 | Crv.2.Pt.5.W |  | supported | RW
51012 | Crv.2.Pt.5.Var |  | supported | RW
51013 | Crv.2.Pt.6.W |  | supported | RW
51014 | Crv.2.Pt.6.Var |  | supported | RW

## 713
Address | Point | Subvalue | Value | R/W | Min | Max | Conformance Notes
51015 | ID |  | 713 | R
51016 | L |  | 7 | R
51017 | WHRtg |  | unimplemented | R
51018 | WHAvail |  | unimplemented | R
51019 | SoC |  | supported | R
51020 | SoH |  | unimplemented | R
51021 | Sta |  | supported | R
|  | OK | supported
|  | WARNING | supported
|  | ERROR | supported
51022 | WH_SF |  | 1 | R
51023 | Pct_SF |  | 0 | R